# EEZ BB3 specification and comparison with the EEZ H24005
#	Feature	EEZ BB3	EEZ H24005
1	Max. number of modules / power outputs (channels)	3 / 6	2 / 2
2	MCU module	STM32F7 MCU board	Arduino Shield r5B12
3	Power module	DCP405 power module or DCM220 dual power module	Power board r5B12
4	Power module topology	Series hybrid (SMPS pre-regulator, linear post-regulator)
5	Floating (isolated) power outputs	Yes
6	Max. output power per channel	155 W
7	Output voltage	0 to 40 V / 80 V (coupled in series)
8	Output current	0 to 5 A / 10 A (coupled in parallel)
9	Current ranges	50 mA / 5 A	500 mA / 5 A
10	Voltage programming resolution	5 mV		10 mV
11	Current programming resolution	5 μA / 0.5 mA	1 mA
12	Voltage readback resolution	5 mV		10 mV
13	Current readback resolution	5 μA / 0.5 mA	1 mA
14	Current ranges switching	Manual / SW auto-ranging
15	Remote sensing / relay switchable	Yes / Yes
16	Remote sensing reverse polarity protection	Yes
17	Remote programming	Yes
18	OVP (Over-voltage protection)	HW, fused / SW	SW
19	OCP (Over-current protection)	SW
20	OPP (Over-power protection)	SW
21	OTP (Over-temperature protection)	SW
22	Reverse power output protection	High power diode, fused	TVS, not fused
23	No. of power relays for output couplings	4 (first two modules outputs in series and parallel, split rail, and ground coupling of all modules)	2 (Outputs in series and parallel)
24	Coupled outputs programming and readback values adjustment (e.g. display up to 80 V instead of two 40 V separately)	Yes
25	Load balancing when outputs are coupled in series or parallel	SW
26	Soft-start/Power-up control	Yes
27	Down-programmer	Yes
28	Output capacitor	33 uF + 470 nF	22 uF + 18 uF + 470 nF
29	Digital/Trigger inputs	2	1
30	Digital outputs	2	1
31	Relay outputs	No	1
32	MCU	STM32F769IIT6	Arduino Due
31	Flash memory	2 MiB	512 KiB
34	System EEPROM	Yes
35	Power module EEPROM	Yes	No
36	TFT Display	4.3” (480 x 272)	3.2” (320 x 240)
37	Touchscreen controller	Resistive
38	Rotary encoder	Yes (Ø31 mm knob)		Yes (Ø19 mm knob)
39	User defined switch	Yes	No
40	Power module communication	Dedicated SPI	Shared SPI
41	Ethernet	10/100 Mbit/s	10/100 Mbit/s
42	USB	FS (full-speed)
43	USB isolation	No	Yes
44	RTC with backup	Yes (replaceable coin battery)	Yes (1 F supercap)
45	Memory card	MicroSD (accessible from front panel)	SD (installed on the TFT display back)
46	Sound	Yes
47	PE terminal	Yes
48	Dedicated Fan controller	Yes, up to 2 fans	No
49	Fan	Ø80 mm, 3- or 4-wire	Ø60 mm, 3-wire
50	Open source firmware	Yes
51	Multi-thread firmware	Yes	No
52	SCPI support	Yes
53	Scripting language	Micro Python	No
54	Programmable output lists	Yes, low jitter	Yes
55	Synchronized OE	Yes	No
56	AC input range	Full range (115 / 230 V)	115 / 230 V (manually switchable)
57	AC input protection	TVS, MOV, SAR
58	Dimensions	290 (W) x 123 (H) x 240 (D) mm	290 (W) x 84 (H) x 238 (D) mm
59	Weight	3.5 kg (with two DCP405 modules)	TBA